## Introduction
Guidance on Remote Services
Introduction to the guidance
"EN 50710:2021 Requirements for the provision of secure remote services for fire safety systems and security systems" has been drafted by CEN/CLC/JTC 4 and published by CEN-CENELEC in 2021. The Euralarm Services section took a leading role in this process with the aim to stimulate the uptake of remote servicing on Fire Safety Systems and Security Systems (FSSS) by providing guidance to service companies and by increasing the acceptance of remote servicing by end-users, insurance companies and response authorities. This remote services standard interacts quite naturally with the corresponding European or national application guidelines for the various types of alarm systems but also interacts with 2 other particular European standards: - "EN 16763:2017 Services for fire safety systems and security systems" providing the minimum requirements for service providers as well as the competencies, knowledge and skills of their involved staff; - "CLC/TS 50136-10:2022 Alarm systems - Alarm transmission systems and equipment - Part 10: Requirements for remote access" provides the detailed technical requirements for the Remote Access Infrastructure (RAI) needed for the delivery of the remote services. This document has been released by CENELEC last August. Being a Technical Specification (TS), the National Standardisation Bodies may publish it in their catalogue but they don’t have to. The interaction between these 3 documents and the concepts introduced in them are complex and Euralarm felt the need to produce the present guidance, especially for micro and small service companies who most often need to subcontract the operation and maintenance of the RAI to a Remote Infrastructure Service Provider (RAISP). The guidance provides an explanation of the main elements of the RAI, including drawings from the standards, and 3 check-lists allowing the service companies to make a self-assessment of their readiness and compliance with the provisions laid down in EN 16763, EN 50710 and CLC/TS 50136-10.
Introduction to the elements of the Remote Access Infrastructure (RAI)
The Remote Access Infrastructure (RAI) is the technical infrastructure that allows and manages the remote access by authorised personnel and third-party systems to associated Fire Safety Systems and/or Security Systems (FSSS). It is made of 3 main functions, usually implemented by software on servers or devices. The core function is the Remote Access Server (RAS). It ensures the adequate routing between a remote user (or remote server) to its assigned FSSS. This routing ensures that a particular user can get access only to the FSSS he has been trained on and authorised to work on. On the user side, the Remote Access Client (RAC) is the function (usually implemented by a software on a server) that authenticates the remote user (or remote server) and requests the RAS to grant him access to the assigned FSSS. On the FSSS side, the Remote Access Endpoint (RAE) is the function (usually implemented by a software or firmware in a Control and Indicating Equipment (CIE) or in an alarm transmitter) that interfaces with the FSSS and manages the secure connection with the RAS. Ensuring security of the remote access is of primary importance. The high-level requirements on the RAI ensuring the security of the remote access are laid down in EN 50710 Clause 4.3.2 and the detailed security requirements are laid down in CLC/TS 50136-10.

## EN50710
EN 50710:2021 CEN/CLC/JTC4 | Remote Services for fire systems and security systems.
This standard specifies the minimum requirements for the provision of secure remote services via a remote access infrastructure carried out either at site or off-site. This standard is intented to support the implementation of the European Service Directive (2006/123/EC) and EN 16763 Services for fire safety systems and security systems.
| Requirement | Chapter | Check
Service organization | Assessment of the risk added | 4.1
| Remote service processes, technologies and communication paths are secure and reliable (design, documentation and holistic testing) | 4.1
| Operation of remote services shall be informed (client, service provider*, MARC*, response authorities*) | 4.6
| Impact assessment of remote service before it is performed | 4.6
| Mitigation measures alligned with risk assessment during the remote service | 4.6
| Funcionality check after the remote service is performed | 4.6
| Remote service requirements are to be applied in conjunction with technical application guidelines | 4.4
RAI | RAI periodic testing, maintenance and update | 4.1
| Training to use RAI within service provider | 4.1
| RAI security supported by state of the art security measures (authentication, authorization, encryption, substitution protection, event logging, traceability). | 4.3
| RAI physical and logical connections monitored for cyber security. | 4.3
RAS | RAS and associated applications are located in -FSSS site, or -MARC (certified in EN50518), or -data centre (certified in EN50600). Service Organizations: certified in EN 16763. | 4.3
| Remote access to the FSSS only via RAS | 4.3 |  | Drawing taken out of EN 5071:2021 Figure 1
RAC | Authorization to access the RAC | 4.3
| RAC sessions automatic termination | 4.3 |  | Abbreviations | Defined terms | Definitions from standard
| Secure access to remote service: - authorized persons per specific operation, list periodically reviewed - access terminals proper location - session automatic termination - connection to RAS is secure | 4.5 |  | FSSS | Fire Safety Systems and/or Security Systems | -
| Define read/control/write operations and assign permisions and restrictions accordingly | 4.7 |  | MARC | Monitoring and Alarm Receiving Centre | continuously manned centre where information concerning the status of one or more FSSS is reported, and additionally where the status of one or more alarm transmission system is monitored
Client | Client informed of remote services | 4.1 |  | RAI | Remote Access Infrastructure | infrastructure incorporating a RAE, RAS, RAC and IT infrastructure
| Contractual agreement between service organization and client | 4.2 |  | RAC | Remote Access Client | software and/or hardware used to gain remote access to functions of one or more FSSS
| Evidence of communication with the client at start and close of control and write functions | 4.4 |  | RAS | Remote Access Server | software and/or hardware used to manage multiple remote connections of multiple FSSS and users
|  |  |  | RAE | Remote Access Endpoint | software and/or hardware endpoint located at site that manages remote access to one or more FSSS

## TS50136-10
TS50136-10 CLC TC79 WG5 | Alarm systems - Alarm transmission systems and equipment - Part 10: Requirements for remote access.
This standard specifies minimum requirements for secure connection and session for remote access to alarm systems. This standard specifies the requirements for the performance, reliability, integrity and security of a Remote Access Infrastructure.
Functionality | Requirement | Chapter | Check
RAISP | Responsible for security measures to protect the RAI | 5
| Shall apply security measures, described in the technical documentation | 5.1
| Data integrity protection following EN50136-1 6.8.1 | 5.2
| Data encryption following EN50136-1 6.8.1 | 5.2
| Only authenticated connections allowed from RAE and RAC to RAS | 5.3
| Two factor authentication | 5.3
| Login attempts restricted to limit risk of brute attack | 5.3
| Timeouts after inactivity | 5.3
| Remote user information inside RAI protected | 5.3
| Remote users or third party systems privileges to the RAI management | 5.4
| Monitor and log authenticated user login and logout, authenticated RAE connections, authenticated RAC connections | 5.5
| Monitor and log modifications to RAI configuration by RAISP | 5.5
| Monitor and log modifications of credentials and privileges | 5.5
| Monitor and log security related events | 5.5 |  | Drawing taken out of CLC/TS 50136-10:2022 Figure 1
| RAI performance criteria and levels agreed. Performance monitoring | 6
| Responsible for documentation (planning, installation, commissioning, service and operation of the RAI) | 7.4 |  | Abbreviations | Defined terms | Definitions from standard
| Responsible for risk management processes (Technology, Continuity Management, Risk Management, Identity Management, Configuration Management, Cyber security) | 8 |  | - | Remote User | person using the RAI via the RAC to remotely access one or more alarm systems
RAE | It shall be authenticated | 5.3 |  | AS | Alarm System | -
| No hardware requirements | 7.3 |  | RAI | Remote Access Infrastructure | system incorporating the logical functions of the RAE, RAS and RAC
| It shall no affect normal operation/performance of the connected alarm system | 7.3 |  | RAC | Remote Access Client | logical function used to gain remote access to functions of one or more alarm systems
| Hosted in the supervised premises | 7.3 |  | RAS | Remote Access Server | logical functions used to manage multiple remote connections of multiple alarm systems and users
RAC | It shall be authenticated | 5.3 |  | RAE | Remote Access Endpoint | logical function that manages remote access to functions of one or more AS
| No physical requirements | 7.1 |  | - | third-party system | system or application communicating with the alarm system via the RAI that is not produced by the RAISP
| Managed by RAISP | 7.1 |  | RAISP | Remote Access Instructure Service Provider | entity responsible for the design, operation and maintenance of the RAI
RAS | It shall be authenticated | 5.3
| No hardware requirements | 7.2
| Hosted in secure location (alternatively located at the supervised premises) | 7.2
| Managed by RAISP | 7.2
Structure | Additional applications for the RAI shall be arranged so that RAI requirements in this TS are still met | 4.1
| RAI shall be designed to only allow connections between RAE and RAS on one end, and between RAS and RAC on the other end. | 4.2
| Connection between RAC and RAE only allowed via RAS | 4.2

## EN16763
EN 16763:2017 CEN-CLC TC4 | Services for fire safety systems and security systems.
This standard specifies the minimum requirements for service providers as well as the competencies, knowledge and skills of their involved staff, regardless whether these services are provided on-site or remotely.
| Requirement | Chapter | Check
General | Note: Annex A for guidance on the documentation of the stages of work | 3.1
| Identification of the service provider (name and trading name, address, authorized person, national registrations,…) | 3.2
| Meet national laws and regulations. | 3.2
| Use this standard requirements only in conjuction with EN standards and national guidelines. | 3.2
| Have resources, knowledge and skills to fulfill the declared services. | 3.2
| Processes to execute the declared services rightfully | 3.2
| Processes to record executed services and mantain these records. | 3.2
| Have executed services in the field of expertise | 3.2
| Initial and ongoing staff training | 3.2
| Insurance for all declared services | 3.2
| Management system that covers the quality of the execution of the declared services | 3.2
| Access to manufacturers' instructions for components and systems for the declared services | 3.2
| Access to the applicable standards, guidelines,… | 3.2
| Keep client related information confidential and secure | 3.2
| Where allowed by regulation and required, provide evidence of security vetting | 3.2
| Use components and systems complying with the existing standards and/or acknowledged rules of technology | 3.2
Subcontracting | Responsibility stays in the service provider | 3.3
| Processes to monitor and manage the quality of subsconstructed services | 3.3
Staff | Identify staff undertaking roles A,B,C | 3.4
| Demonstrate adequate numbers to support the service provided | 3.4 |  | Flow chart taken out of EN 16763 Figure 2
| Role A (decision-making authority + responsability for compliance). - level 5 of EQF within the declared services, or -realizing 3 systems in the last 5 years in the declared services | 3.4
| Role B (self management and supervision of the routine work of others, some responsibility for the evaluation and improvement of work). - level 4 of EQF within the declared services, or -realizing 3 systems in the last 3 years in the declared services | 3.4
| Role C (fullfilling assigned tasks in a reliable way). - level 3 of EQF | 3.4
Service output | Processes for defining and documenting the output of a stage of work: - alligned with the relevant application guide - in accordance with local requirements - change control - identify the responsible person | 3.5
| Requirements for maintenance providers: - staff with the right knowledge, skills and competences - maintenance in accordance with contract and manufacturer's specifications - service output in accordance with general requirements, client informed. | 3.5

## General information
Foreword
This Guidance Note is intended as a general guidance and is not a substitute for detailed advice in specific circumstances. Although great care has been taken in the compilation and preparation of this publication to ensure accuracy, Euralarm cannot in any circumstances accept responsibility for errors, omissions or advice given or for any losses arising from reliance upon information contained in this publication.
Change revisions
Date: November 2022
Change: First release
Disclaimer
This document is intended solely for guidance of Euralarm members, and, where applicable, their members, on the state of affairs concerning its subject. Whilst every effort has been made to ensure its accuracy, readers should not rely upon its completeness or correctness, nor rely on it as legal interpretation. Euralarm will not be liable for the provision of any incorrect or incomplete information.
Note: The English version of this document is the approved Euralarm reference document.
Copyright Euralarm
© 2022, Zug, Switzerland
Euralarm · Gubelstrasse 11 · CH-6300 Zug · Switzerland
E: secretariat@euralarm.org
W: www.euralarm.org